## Slide 1: Modeling a PCM storage unit for solar thermal cooling in Masdar City
Irene Rubalcaba Montserrat
RSC Members:
Dr. Matteo Chiesa
Dr. Peter Armstrong
Dr. Ali Abbas
Notes: Thank you for coming to my defense.. The title of my thesis is “Modeling a PCM storage unit for solar thermal cooling in Masdar City
My research committee members are Dr. Chiesa, Dr. Armstrong and Dr. Abbas.

## Slide 2: Solar cooling system
Solar Field
Charging mode
Discharging mode
PCM
Storage
Unit
Drum
Condenser
Evaporator
Pump
Heat Exchanger
Generator
Pump
Absorber
Cooling System

## Slide 3: Power profile from the Beam Down [kW]
Chart: Time [hrs]
21st of March 2011

## Slide 4: Supply and demand disparity storage opportunity
Chart: Q [kW]
| 0.41666666666666691 | 0.45833333333333326 | 0.5 | 0.54166666666666652 | 0.58333333333333337 | 0.62500000000000033 | 0.66666666666666663 | 0.7083333333333337 | 0.75000000000000033 | 0.79166666666666652 | 0.83333333333333304
Cooling load- 4 Buildings | 0 | 90.6 | 101.6 | 106.1 | 95.3 | 93.5 | 89.3 | 73.5 | 58.5 | 49.5 | 0
Power from the Beam Down | 0 | 26.4 | 61.5 | 88.9 | 111.4 | 120.5 | 127 | 128.1 | 112.7 | 84.7 | 53.6 | 19.2 | 1.1 | 0

## Slide 5: Supply and demand disparity storage opportunity
Chart: Q [kW]
| 0.4166666666666668 | 0.45833333333333326 | 0.5 | 0.54166666666666652 | 0.58333333333333337 | 0.62500000000000011 | 0.66666666666666663 | 0.70833333333333348 | 0.75000000000000011 | 0.79166666666666652 | 0.83333333333333304
Cooling load- 4 Buildings | 0 | 90.6 | 101.6 | 106.1 | 95.3 | 93.5 | 89.3 | 73.5 | 58.5 | 49.5 | 0
Power from the Beam Down | 0 | 26.4 | 61.5 | 88.9 | 111.4 | 120.5 | 127 | 128.1 | 112.7 | 84.7 | 53.6 | 19.2 | 1.1 | 0
Extra heat to store
Storage use

## Slide 6: STORAGE MODELING Geometry
CYLINDRICAL STORAGE COMPARTMENT
Length=11m
COPPER PIPE
Length=11m
Outside Diameter= 0.012m
Thickness=1mm

## Slide 7: Modeling phase change using COMSOL
Melting range = ΔTm
ΔTm = 490 to 493 K
Cp= 1330 + Latent heat/ΔT
FULLY SOLID
Cp = 1330 [J/KgK]
FULLY LIQUID
Cp = 1330 [J/KgK]

## Slide 8: Numerical modeling
Problem Type: Transient Thermal Fluid
Model Used: Time depending - Non Isothermal flow
Incompressible Navier- Stokes:
Heat Transfer by conduction and convection:
Geometry is considered 2D axial symmetry

## Slide 9: 2D Axial symmetry model
Maximum Energy Storage
Capacity:
400 [MJ] + Sensible Heat

## Slide 10: Numerical Results for 44 tubes after 20700 seconds - 5.75 hr
Enthalpy
Temperature

## Slide 11: Mesh Sensitivity
Mesh Type | Extremely Fine | Normal | Coarser
Number of elements | 536,068 | 88,946 | 82,327

## Slide 12: Effect of fins
No fins
5 Fins
10 Fins
20 Fins

## Slide 13: Effect of inlet velocity
v= 0.0932 m/s
v= 0.0832 m/s
v= 0.07992 m/s
v= 0.07629 m/s

## Slide 14: Solidification temperature outlet
Chart: Storage discharge temperature[K]

## Slide 15: Final Design
81 tubes
L =11m
ri= 1 cm
r0= 3 cm
Total volume= 5.7m3
Total PCM mass = 4.209 tons
Maximum storage capacity
= 400[ MJ] + sensible heat
Symbol | Description | Value | Units
 | Latent heat of fusion of the PCM | 95000 | 
 | Density of the PCM | 1880 | 
 | Specific heat of the PCM | 1330 | 
 | Thermal conductivity of the PCM | 4 | 
αpcm | Thermal diffusivity |  | 
 | Melting Temperature of the PCM | 493 / 220 | K / C
Material= KNO3-NaNO3(eu)