
ASHRAE Transaction 119(1)


Optimal coordination of heat pump compressor and fan speeds and subcooling over a wide range of loads and conditions
Tea Zakula (tzakula@mit.edu)1, Peter Armstrong2, Leslie Norford1
1Massachusetts Institute of Technology, Cambridge, MA

2Masdar Institute of Science and Technology, Abu Dhabi, UAE
ABSTRACT 

Advanced cooling systems with high-temperature cooling (sensible only), night precooling, and highly efficient variable-speed compressors, fans and pumps can benefit from on-line model predictive control to find and continually update optimal daily (or weekly) precooling sequences. As a part of the model predictive control, it is desirable to use optimized plant-specific control laws to match compressor, fan and pump speeds to required capacity. A previous paper presents a modular heat pump model that simulates steady-state performance over the wide ranges of lift (external pressure ratios from <1 to 6) and capacity (10:1 turndown) that could be explored in the search for optimal solutions. This paper describes the adaptive grid search technique used to map optimal heat pump performance as a function of the capacity and indoor and outdoor temperatures. The grid search finds optimal condenser and evaporator airflows and optimal subcooling at each operating point.  The method is illustrated for a number of cases including two-compressor systems and refrigerants R410A, R600 (propane), and R717 (ammonia). The extreme non-linearity of optimal fan-speed control laws is demonstrated.  The impact of zero subcooling with respect to optimal subcooling is assessed for the single compressor machines.  The specific power at optimal fan speeds, as a function of capacity and indoor-outdoor temperature, is compared for R410A, propane, and ammonia-charged machines. Finally, the question of optimal sizing of optimally controlled variable-speed heat pumps is explored and it is shown that modest oversizing is desirable. These findings suggest that the relative sizing of heat pump components—compressor, compressor motor, condenser and evaporator—as well as the sizing of the heat pump itself relative to design load, may benefit from a thorough reassessment of current practice.  
INTRODUCTION


One attractive way to achieve efficient cooling in buildings is to combine efficient, optimally controlled thermal energy storage (TES), high-temperature distribution, such as chilled beams, and a cooling plant that operates efficiently over a wide range of lift and part-load fractions. This combination of components and controls may be called a low-lift cooling system (LLCS). In simulations with idealized TES, annual cooling system energy savings of up to 75% were found compared to a baseline ASHRAE 90.1-2004 VAV system (Jiang 2007, Armstrong 2009, Katipamula 2010). Initial verification of these results was provided by Gayeski (2010) for a typical summer week for Atlanta and Phoenix in a climate chamber experiment using the identical outdoor unit (compressor, condenser and fan) for both the low-lift and baseline configurations. Since optimization and control are critical for maximizing the benefits of the low-lift cooling system, an important part of the low-lift cooling technology is model predictive control, an algorithm that optimizes the system’s operation given a thermal response model of the building and weather forecasts. Another key optimization question is the coordination of condenser and evaporator fan and/or pump speeds with compressor speed to satisfy any given load under any given conditions.  This process is known in the HVAC literature as static optimization (Chapter 42, ASHRAE 2011). Although the use of empirical data (Gayeski 2011) is unavoidable for modeling building transient thermal response, heat pump performance can, in principle, be more easily and reliably characterized by the use of engineering models. However, heat pump manufacturers’ data are often only available for a limited range of operating conditions and capacity. This makes it nearly impossible to analyze systems that operate outside those conditions or systems that are still commercially unavailable. Therefore, to perform static optimization, a heat pump model that is accurate, yet computationally inexpensive, is required.

The only model found in the literature that has been used to perform static optimization based on a physical heat pump model is the model developed by Armstrong (Jiang 2007 and Armstrong 2009). Two optimization variables are the evaporating and condensing temperatures, which can then be related to the optimal evaporator fan, condenser fan and compressor speeds. The model assumes constant evaporating and condensing temperatures without evaporator superheating, condenser subcooling, or heat pump pressure drops. It also assumes constant conductance (U-value) for the evaporator and condenser, independent of refrigerant and air/water flow rates. Zakula et al. (2011) showed that even neglecting pressure drops can lead to serious errors in power consumption predictions and, therefore, this model would need to be extended for better parameter predictions. There are numerous physical models found in the literature that do not perform optimization, but do calculate steady state heat pump performance and, hence, could potentially be adopted for optimization purposes. However, they vary from complex models that are computationally expensive and require a large number of input parameters, to models that are similar to Armstrong’s model, in that they are relatively simple and fast, but do not take into account certain important phenomena. A more detail literature review on heat pump modeling is given in Zakula (2010).

Though they do not describe the optimization of an individual heat pump’s performance, related works on the optimization of large chiller plants can be found in the literature. Lau et al. (1985) developed a TRNSYS model to analyze different control strategies for an existing chiller plant with four centrifugal chillers, a cooling tower and chilled water tanks. For a given cooling load and wet-bulb temperature, the cooling tower fan speed, condenser pump flow and number of chillers were optimized for minimal power consumption. The power consumption of each chiller is characterized as a function of the cooling load, leaving chilled water temperature and leaving condenser water temperature using curve fits to manufacturer’s data. Braun et al. (1987a) investigated the performance and optimal control of a large chiller plant equipped with a cooling tower. A simplified model was used to find near-optimal control with the cooling tower airflow and condenser water flow rates as the control variables. For an individual chiller, measured data from the existing plant were fit to curves that define the chiller power as a function of the cooling load and temperature difference between the leaving condenser and chilled water flows. In subsequent work (Braun et al. 1989), the system was extended to include the chilled water loop and the air handlers with the five independent control variables of supply air set temperature, chilled water set temperature, cooling tower airflow, condenser water flow and the number of operating chillers. Braun’s more recent work on chiller plant optimization (Braun 2007) analyzed near-optimal control strategies for a hybrid cooling plant powered by electricity and natural gas. The optimization objective function was the operating cost, which includes the electrical and gas energy cost, electrical demand cost and maintenance cost. King and Potter (1998) developed a model of a cooling plant with ice thermal storage to analyze conventional and optimal plant control. For a given cooling load, return air (zone) temperature, wet bulb temperature and state of charge, the model optimizes the thermal-storage discharge rate and the chilled-water and supply-air temperature set points for the lowest system power consumption, including the chiller, pumps, cooling-tower fan and supply- and return-air fans. Similar to the previous chiller plant optimization models, performance of an individual chiller is captured using curve fits to manufacturer’s data.  

Our objective here is to use optimization to better understand the extent to which heat pump and distribution system design and control improvements can impact the annual energy use of advanced cooling systems. 
MODEL DESCRIPTION

Optimization is performed using the steady state heat pump model developed by Zakula et al. (2011) that can simulate the performance of different heat pump types, such as air-to-air heat pumps and air- and water-cooled chillers. The model is developed from first-principle models of the evaporator and condenser, and a semi-empirical compressor model. It takes into account pressure drops in the heat pump, the dependence of heat transfer coefficients on flow rates, superheating in the evaporator and desuperheating and subcooling in the condenser. A modular approach offers the possibility of choosing between different simulation options (level of complexity) and makes the model easy to expand and customize. The model can be used for a single- two- or variable-speed compressor, single compressor, multiple parallel compressors, evaporators or condensers, as well as for different refrigerants. The inverse heat pump model with a compressor frequency as an input has also been developed and is used to optimize a heat pump with a two-speed compressor, the base case for the annual energy consumption assessments presented in this paper.
The optimization input parameters are the cooling load (Q), zone temperature (Tz) and outside temperature (To), and the optimization variables are the evaporator airflow rate (Vz), condenser airflow rate (Vo) and condenser area ratio devoted to subcooling (ysc). If one wants to optimize only one or two variables, the other variables need to be given as an input, e.g. one may want to know the performance impact of the optimal subcooling as opposed to zero subcooling, in which case zero subcooling area is specified and the condenser and evaporator air or water flow rates are optimization variables. All other heat pump operating variables are functions of the optimization variables; in particular, for optimal control, one is mainly interested in the optimal evaporator fan speed, condenser fan speed and compressor speed. One may also be interested in the related refrigerant mass flow rate, evaporating temperatures and pressures, condensing temperatures and pressures, suction and discharge state, subcooling temperature difference and total power consumption.  

The optimization algorithm uses the grid search method shown in Figure 1, which ensures finding the global minima without convergence difficulties. For each set of input parameters (Q, Tz, To) there are two loops, the outer loop for the optimal subcooling area ratio search, and the inner loop for the optimal flow rates search. The initial 3 by 1 grid (A-grid) and 3 by 3 grid (B-grid) are created for the outer and inner loops respectively. First, the total power consumption is calculated for each of the nine B-grid points and ysc=ysc{1}. 
If the lowest power is anywhere on the B-grid boundaries, the grid is extended according to Figure 2, and total powers are evaluated for new points. The process continues until the lowest power is in the middle B-grid point (B{2,2}), in which case the algorithm moves to the second A-grid point (ysc{2}). Similar to the B-grid, if the sub-optimization finishes for all three A-grid points and the lowest power is on the A-grid boundaries, the A-grid extends until the optimum is at the middle A-grid point (A{2}). 

The optimization process is further accelerated with the step adaptation, in which after finding the optimal variables with a larger step, a new 5 by 5 B-grid is created using a smaller step (half the large step) and Vz_opt and Vo_opt as the central grid point (Figure 3). Since the power consumption in nine points is already known from the previous (large step) grid search, only sixteen additional function evaluations are performed. The point with the lowest power is assigned as the final optimal point (new Vz_opt  and Vo_opt). The same is applied for the optimal subcooling search. 

PERFORMANCE MAP RESULTS
For a given cooling rate, outside and zone temperature, the result of the static optimization provides the optimal set of the evaporator and condenser airflow rates, compressor speed and subcooling for which the power consumption will be the lowest. To show the broad utility and potential benefits of optimization using a component-based model the optimization is performed for several different scenarios: 

a)  air-to-air heat pump with a single compressor (variable-speed rolling-piston compressor) and R410A as a refrigerant

b)  air-to-air heat pump with two parallel compressors, evaporators and condensers (two variable-speed rolling-piston compressors) and R410A as a refrigerant

c)  air-to-air heat pump with a single compressor (variable-speed rolling-piston compressor) and ammonia (R717) as a refrigerant 

d) air-to-air heat pump with a single compressor (variable-speed rolling-piston compressor) and propane (R600) as a refrigerant


The optimization is performed with a 0.025 m3/s step for the airflows (0–0.3 m3/s and 0–0.7 m3/s airflow range for the evaporator and condenser fan respectively) and a 0.001 step for the condenser area ratio devoted to subcooling.


For the heat pump with a variable-speed compressor and R410A as a working fluid, the optimal set of evaporator and condenser airflow rates (Figure 4), compressor speed (Figure 5) and subcooling (Figure 6), for which the power consumption for cooling (Figure 7) will be the lowest, is shown for the outside temperature To =30oC. Figure 4 shows that the evaporator and condenser airflows are a strong function of part-load ratios. Furthermore, it was noticed that when optimizing the airflows, the parameter indirectly being optimized is the temperature difference. For a given cooling rate, the optimizer tries to maintain the optimal temperature difference on the evaporator (between the evaporating and air temperature) and the condenser (between the condensing and air temperature), regardless of the zone or ambient temperature. From Figure 7, which shows the specific power as a function of part-load ratios, it can be seen that the heat pump efficiency increases with lower part-load ratios. This raises the question of the appropriate heat pump “external sizing,” since with modest oversizing, the heat pump will run at higher efficiencies. However, because there is a cost penalty associated with a size increase, both size and initial cost need to be carefully balanced. The optimal “external sizing” for the lowest energy consumption is discussed later in the paper. Besides “external sizing,” which refers to appropriate sizing of the heat pump as a whole, another interesting topic to be addressed is “internal sizing:” the sizing of each heat pump component, primarily the evaporator, condenser and compressor. Although not included as a part of this analysis, the presented heat pump optimization algorithm could be extended to the component-sizing problem given a joint distribution of cooling load and operating conditions.
The optimal results are presented here over a wide range of loads (0.1–1.0 part-load ratio) and temperature differences (0–30oC difference between the zone and ambient). Although Figure 4 indicates nearly linear trends for the evaporator and condenser airflows, it can be seen from Figure 8 that the same is not true for the optimal airflow-to-compressor-frequency ratio due to non-linearity in compressor frequency trends. Similar to optimal airflows, Figure 9 shows a strong dependence of the optimal subcooling on the part-load ratio. Finally, it can be seen from Figure 10 that the optimal specific power is almost solely a function of part-load ratio and (for moderate range of evaporating temperature) of temperature differences between the zone and outside. This is in agreement with the study done by Braun (1987b) that concludes that the chiller power consumption is primarily a function of cooling load and the temperature difference between the leaving condenser and chilled water streams. It is important to point out that the optimal evaporator airflows at high part-load ratios are significantly higher than the maximum feasible for the specific heat pump (the airflow rate at the maximum evaporator fan speed was around 0.15 m3/s for the real heat pump). Because manufacturers primarily optimize this type of heat pump for the dehumidification mode, in which the heat pump would run with much lower evaporator fan speeds, their use for only sensible cooling results in fan speeds that are far from optimal. The consequence of this for the total energy consumption is shown in the following example.
Subcooling has been used as one of the optimization variables considering that heat pump manufacturers have the means of controlling subcooling by placing an additional valve between the condenser and liquid receiver. The impact of optimal subcooling with respect to zero subcooling is assessed. Figure 11a shows that the COP differences, although relatively small, increase for higher part-load ratios and temperature differences. As a result, the average annual COP of a system that operates at lower part-load ratios would be much less influenced by non-optimized subcooling compared to prevailing systems that deliver most of their annual cooling effect at high part-load ratios. The COP relative differences in Figure 11a are calculated as:



[image: image1.emf]


COP relativedifference =
COPoptimized −COPzero subcooling



COPoptimized










COPrelativedifference

=

COP

optimized

-

COP

zerosubcooling

COP

optimized


(1)
An additional analysis was done to assess the impact of the optimized airflows with respect to fixed airflows. Fixed airflows were set to the maximum feasible for the specific heat pump (0.15 m3/s and 0.77 m3/s for the evaporator and condenser fan respectively), and the subcooling was set to zero. The results (Figure 11b) show significant differences in the specific power between the optimal and non-optimal cases.  This leads to the conclusion that optimizing the airflows plays a significant role in the heat pump performance, and that heat pumps optimized for dehumidification mode can significantly underperform energy-wise when used for sensible cooling only. The COP relative differences in Figure 11b are calculated as:


[image: image2.emf]


COP relativedifference =
COPoptimized −COPnon−optimized



COPoptimized










COPrelativedifference

=

COP

optimized

-COP

non

-

optimized

COP

optimized


(2)

It can be seen in Figure 7 and Figure 10 that due to inverter losses the specific power increases for part-load ratios less than 0.2. The inverter losses account for a small portion of the total power at higher part-load ratios but become more important as the cooling load decreases. Recently, manufacturers have started to design heat pumps with two, rather than one, variable-speed compressors, which can help to avoid high inverter losses at lower part-load ratios and result in better overall heat pump performance. This case has been analyzed by optimizing the heat pump with 2X scaling of evaporators, condensers and piping and two variable-speed rolling-piston compressors. The optimization algorithm tests both cases and decides if it is more efficient to run both or just one of the compressors.  The results of the analysis (Figure 12) show that the heat pump design with two parallel compressors can significantly improve the performance at low part-load ratios by running only one of the two inverter-compressor subsystems. 

When the outside temperature is lower than the zone temperature, a heat pump can run in an economizer mode in which only the evaporator and condenser fans are running and the compressor is turned off. In some cases liquid may flow from condenser to evaporator by gravity while in others the flow may be assisted by a small efficient hermetic pump (NTDP 1994). Having a lower outside temperature, however, does not necessarily imply that running in the economizer mode is more energy efficient. For small temperature differences relative to a part-load ratio, the total sum of the fan and compressor power can be lower than the sum of fan powers when operating in the economizer mode due to high fan speeds. Therefore, without having detailed heat pump maps for both modes (Figure 13), it is hard to develop an appropriate control algorithm that regulates switching between the two. Figure 13a illustrates the slope discontinuity where the compressor-mode and economizer-mode regions intersect, and Figure 13b shows how the intersection moves for different outside temperature. The combined heat pump map is created (Figure 14) using the optimization results and an algorithm that based on the lower power consumption decides which mode to use when To < Tz.

The heat pump model and the optimization algorithm can also be used to analyze how changing refrigerants might influence the heat pump performance. When switching to refrigerants other than R410A, the heat pump geometry (primarily the compressor displacement volume and refrigerant piping) was adapted to account for differences in density and heat of vaporization. The compressor displacement volume is scaled using:



[image: image3.emf]


Drefrigerant = DR410A
ρR410A
ρrefrigerant



hlg,R410A
hlg,refrigerant










D

refrigerant

=

D

R410A

r

R410A

r

refrigerant

h

lg,R410A

h

lg,refrigerant


(3)

The largest pressure drop in the evaporator that corresponds to 4oC drop in the saturation temperature (at Tz=18oC, To=45oC and Q=Qmax) for R410A was used to find the appropriate scaling factors for the refrigerant piping. The scaling factors found to give the pressure drop that correspond to the same 4oC drop in the saturation temperature are 0.9 for ammonia, and 1.37 for propane. The relative differences in COP for different refrigerants are shown in Figure 15. The COP relative differences in Figure 14 are calculated as:



[image: image4.emf]


COP relativedifference =
COPrefrigerant −COPR410A



COPR410A










COPrelativedifference

=

COP

refrigerant

-COP

R410A

COP

R410A


(4)
ANNUAL PERFORMANCE RESULTS
How will switching to a heat pump with a single two-speed compressor, double compressors, different refrigerants, or a heat pump with non-optimal airflows or non-optimal subcooling can influence annual energy consumption?  Cooling loads used for this analysis are the results of the study done by Armstrong et al. (2009) for a typical office building in Chicago. They are presented in Figure 16 for two different cases as full-load-equivalent operating hours (FLEOH), a function of part-load ratio and outside temperature. Load distribution A represents instantaneous loads for a building without thermal energy storage, while Load distribution B represents loads that are shifted towards lower part-load ratios and lower outdoor temperatures using thermal energy storage and daily optimized precooling.  Load distribution B assumes hydronic radiant cooling, ideal thermal storage, variable-speed chiller and a dedicated outdoor air system for ventilation. Although the shifted load distribution will be affected by the exact performance characteristic of the heat pump or chiller, we assume that the distribution presented here is representative of the class of static-optimized machines with high-turndown variable-speed compressors, pumps and fans.

Cooling loads for two cases were convolved with several different heat pump performance maps, results of static optimization, to estimate their influence on the annual energy consumption. Performance maps are created for the following heat pumps:

1. variable-speed compressor heat pump with optimized airflows and subcooling 

2. variable-speed compressor heat pump with optimized airflows, assuming zero subcooling

3. variable-speed compressor heat pump with non-optimized airflows and subcooling (assuming zero subcooling, and maximal airflows Vz=0.15 m3/s, Vo=0.77 m3/s)

4. two-speed compressor heat pump (assuming two-speed fans)
5. double variable-speed compressor heat pump with optimized airflows and subcooling 

For the heat pump with a two-speed compressor, subcooling is optimized for compressor speeds of f=0.5fmax and f=fmax,. For this case the fans were also assumed to be two-speed, with airflows set at the optimal values found for the variable-speed heat pump (Case 1) at 0.5Qmax (used at the low-frequency compressor speed) and Qmax (used at the high-frequency speed). For part-load ratios other than Q=0.5Qmax and Q =Qmax, it has been assumed that the compressor cycles between f=0, f=0.5fmax, and f=fmax. The specific power (1/COP) for those cases is calculated using equations given in Armstrong et al. (2009):



[image: image5.emf]


tH = 2 Q
Qmax



−1










t

H

=

2

Q

Q

max

-

1


(5)

where tH is high-speed duty fraction. 

if tH < 0



[image: image6.emf]


1
COP



= 1
COP (at To and f = 0.5fmax )










1

COP

=

1

COP(atT

o

andf

=

0.5f

max

)


(6)

else



[image: image7.emf]


1
COP



= 1− tH( ) 1
COP (at To and f = 0.5fmax )



+ tH
1



COP (at To and f = fmax )










1

COP

=

1

-

t

H

( )

1

COP(atT

o

andf

=

0.5f

max

)

+

t

H

1

COP(atT

o

andf

=

f

max

)


(7)

For the cases 1 through 5, additional optimization was done for the refrigerant-side economizer mode. Combined heat pump maps, similar to the one in Figure 14 (compressor mode and economizer mode), were created using an algorithm that decides which mode uses less power for a given cooling load, zone and outside temperature.

The annual energy consumption is calculated by comparing FLEOH distributions (A or B) with different heat pump performance maps (Case 1 – Case 5):



[image: image8.emf]


E = FLEOHi, j
1



COPi, jj
∑



i
∑ Qmax










E

=

FLEOH

i,j

1

COP

i,j

j

å

i

å

Q

max


(8)
where i = Q/Qmax and j = To. Although FLEOH and COP are in general a function of Tz, To and part-load ratio (Q/Qmax), in this analysis we assume Tz = 22oC. 

The results presented in Table 1 show that with precooled thermal energy storage airflow optimization is considerably more important than subcooling optimization. The annual energy savings for the optimal case compared to the non-optimal case (with fixed airflows and zero subcooling) were around 50%, while the savings were only slightly less (around 0.4%) for the optimal case compared to the case where subcooling was not optimized. It has also been shown in Table 1 that a heat pump with double compressors saves a significant amount of energy, especially for systems that operate at lower part-load ratios most of the time. 

	Table 1. Annual energy savings for different cases with R410A

	Optimized versus zero subcooling

(B1 versus B2) 
	(Ezero_sc – Eoptimized)/Ezero_sc
	0.4 %

	Optimized versus non-optimized

(B1 versus B3)
	(Enon-optimized – Eoptimized)/Enon-optimized
	49.6 %

	Double versus single compressor 

(B1 versus B5)
	(Esingle – Edouble)/Esingle
	11.9 %



Results in Table 2 show that a variable-speed compressor heat pump (Case 1) enables large energy savings compared to a two-speed compressor heat pump (Case 4) whether one is mostly operating at higher (Distribution A) or at lower (Distribution B) part-load ratios. The Armstrong’s study assumed a two-speed compressor heat pump for Distribution A, and a variable-speed compressor heat pump for Distribution B. The results of this analysis (Table 2, Column 4) show that in addition to the variable-speed compressor savings (around 30%), the additional savings (around 20%) are achieved by operating the heat pump at lower part-load ratios. However, as shown in Table 2, not all heat pumps benefit equally from the variable-speed compressor usage or the operation at lower part-load ratios. Hence, for a better understanding of the heat pump performance when switching to different refrigerants (Table 3) the optimization algorithm presented here has shown to be extremely advantageous. 

	Table 2. Annual energy savings for Distribution A and Distribution B using two-speed and variable-speed compressor heat pumps

	
	A1 versus A4

(EA4 – EA1)/ EA4
	B1 versus B4

(EB4 – EB1)/ EB4
	A4 versus B1

(EA4 – EB1)/ EA4

	R410
	29.4 %
	34.5 %
	48.6 %

	Ammonia
	20.1 %
	21.6 %
	38.3 %

	Propane
	7.4 %
	12.6 %
	28.6 %


	Table 3. Annual energy consumption comparison between different refrigerants for B1 scenario

	
	(Erefrigerant – ER410A)/ER410A

	Ammonia versus R410A
	-8.7 %

	Propane versus R410A
	-2.4 %



Using the same annual FLEOH distributions (Figure 16), an optimization is performed to find the heat pump sizing factor that minimizes energy consumption for scenarios A1 (Distribution A with variable-speed heat pump), A4 (Distribution A with two-speed heat pump), and B1 (Distribution B with variable-speed heat pump). Figure 17 shows how different sizing factors influence the total annual energy savings compared to the nominal size system. The gradient-based optimization algorithm in MATLAB determined for this particular case that the optimal sizing factor for the B1 would be 1.17, meaning that in this scenario the heat pump has near-optimal size. Furthermore, the additional energy savings of the optimally sized system were very small compared to the nominally sized system. The heat pumps for A1 and A4 scenarios, on the other hand, are far from the optimum. The optimum that would be achieved with 2.5 sizing factor for A1 and 1.9 sizing factor for A4 would result in energy saving of approximately 20% for A1 and 17% for A4 compared to the nominal size system. Note that heat pump capital cost is not considered here, but also that the savings for an optimally sized heat pump are achieved almost entirely by increased evaporator and condenser size. Hence, its capital cost can be reduced without much impact on annual energy consumption by using a much smaller compressor (ADL 2000, Levins et al. 1997).
SUMMARY

An optimization algorithm that uses an adaptive grid search method is developed for a heat pump static optimization over a wide range of conditions and loads. For a given cooling rate, zone and outside temperature, the algorithm finds the optimal evaporator airflow, condenser airflow and subcooling, for which the total power consumption in minimal. All other heat pump parameters, such as the compressor frequency, refrigerant mass flow rate, temperatures and pressures are functions of the given inputs and optimization variables. The algorithm can be used to optimize an air-to-air, water-to-air and water-to-water heat pump with any refrigerant supported by software REFPROP (Lemmon et al. 2007). It can also be used for different heat pump types, such as heat pumps with a single or multiple evaporators, compressors and condensers, heat pumps with single- double- or variable-speed compressors, as well as heat pumps with different compressor types.


The optimization results for an air-to-air heat pump with single rolling-piston compressor and R410A as a working fluid have been presented over a wide range of conditions and loads. It is shown that the COP and optimal subcooling are almost solely functions of a part-load ratio and temperature difference between a zone and outside. It has also been shown that the COP increases for lower part-load ratios, which suggests that modest oversizing of optimally controlled variable-speed heat pumps is desirable.

The case with zero subcooling and optimized airflows has been compared to the optimized heat pump performance. Although relatively small (0–5 %), the COP benefits of subcooling increase for higher part-load ratios and larger temperature differences. The importance of airflow optimization was demonstrated analyzing the case with fixed airflows, in which case the COP values were significantly lower compared to the optimal case. Furthermore, the results show that a heat pump primarily optimized for dehumidification mode can significantly underperform when used for sensible cooling only.

The specific power of a heat pump with a single compressor increases for very low part-load ratios (less than 0.2 in this example) mainly because of inverter losses. One of the possible improvements analyzed here is a heat pump with two parallel compressors. For part-load ratios lower than 0.5 the control algorithm decides if it is more efficient to run one or two compressors, while for the higher part-load ratios both compressors operate in parallel. The results of this analysis show significant improvement at lower part-load ratios when two parallel compressors are used. 

Although an economizer mode can be used when the outside temperature is lower than the inside temperature, it has been shown that the economizer mode is not always more economical. The optimization algorithm can be used here to decide whether the compressor mode or economizer mode uses the least amount of energy.

The advantage of the optimization algorithm was also demonstrated comparing the performance of an ammonia and a propane heat pump against an R410A heat pump. Using the optimization algorithm it was possible to predict the performance of a heat pump when switching to different refrigerants, which would be difficult to predict otherwise since it varies significantly with the change of refrigerant.

The annual energy consumption has been compared among different cases using the sensible cooling load distribution for a typical office in Chicago. For this particular example, the system with optimized variables annually saves approximately 50% of energy compared to the non-optimized system, which indicates the importance of heat pump static optimization and the model predictive control of thermal energy storage. The system with variable-speed compressor that operates at night by precooling and at lower part-load ratios most of the time saves a significant amount of energy compared to the system with two-speed compressor that operates at higher part-load ratios. It is also shown that the system can benefit from a heat pump with double compressors that work in parallel since this reduces inverter losses at low part-load ratios. Furthermore, optimization has been used to find the optimal heat pump sizing. For the system that operates at higher part-load ratios most of the time, the optimal sizing resulted in approximately 17 – 20 % annual energy saving compared to the nominal system size.


In conclusion, the algorithm presented here can be used to optimize heat pump performance over a wide range of operating conditions and loads and to optimize the heat pump size. This can be particularly beneficial for novel systems, for which curve fits to the optimization results could easily be implemented as a part of a building predictive control. The algorithm can also be used to analyze the influence of different optimization variables or to compare heat pumps with a different combination of components or different refrigerants. 
Acknowledgments

The authors wish to acknowledge MIT Energy Initiative, Masdar Institute of Science and Technology, and Martin Family Society for their support of this research. Thanks to Pacific Northwest National Laboratory for the result of their study on low-lift cooling technology, to Eric Lemmon from National Institute of Standards and Technology for support with software REFPROP, and to Dr. Piotr Domanski for his help regarding the appropriate sizing when switching to different refrigerants. 
NOMENCLATURE
Symbol
Description




                 Unit

D


compressor displacement
m3
COP
coefficient of performance
-
E


energy
J
f


compressor shaft speed
Hz

h


enthalpy
J/kg

Q 


cooling rate 
W

T


temperature 
K

tH


high-speed duty fraction
-

y


condenser area percentage
-



refrigerant density at suction conditions
kg/m3
Subscripts


fg


refers to change from saturated liquid to saturated vapor



max

maximal
o


outside
opt


optimal

sc


subcooling region of condenser


z


zone

REFERENCES 

ADL. 2000. Energy efficient rooftop air conditioner: continuation application technical progress statement. Project DE-FC26-99FT40640, Arthur D. Little, Inc., Cambridge, MA
Armstrong, P. R., W. Jiang, D.W. Winiarski, S. Katipamula, L.K. Norford and R.A. Willingham. 2009.  Efficient low-lift cooling with radiant distribution, thermal storage and variable-speed chiller controls–Part I: Component and subsystem models.  ASHRAE HVAC&R Research, 15(2):366-401. 
Armstrong, P. R., W. Jiang, D.W. Winiarski, S. Katipamula, L.K. Norford and R.A. Willingham. 2009.  Efficient low-lift cooling with radiant distribution, thermal storage and variable-speed chiller controls – Part II: Component and subsystem models.  ASHRAE HVAC&R Research, 15(2):402–432.
ASHRAE. 2011. 2011 ASHRAE Handbook–Applications. Atlanta: American Society of Heating, Refrigerating and Air-conditioning Engineers, Inc.

Braun, J.E., J.W. Mitchell, and S.A. Klein. 1987a. Performance and control characteristics of a large cooling systems. ASHRAE Transactions 93(1):1830–52.
Braun, J.E., J.W. Mitchell, S.A. Klein. 1987b. Models for variable-speed centrifugal chillers. ASHRAE Transactions 93(1):1974–813.

Braun. J.E., S.A. Klein, W.A. Beckman and J.W. Mitchell. 1989. Methodologies for optimal control of chilled water systems without storage. ASHRAE Transactions 95(1):652–62.
Braun, J.E. 2007. Near-optimal control strategies for hybrid cooling plans. International Journal of HVAC&R Research 13(4):599–622.

Gayeski, N. 2010. Predictive Pre-cooling Control for Low Lift Radiant Cooling Using Building Thermal Mass. Doctoral dissertation, Massachusetts Institute of Technology.
Gayeski, N.T., T. Zakula, P.R. Armstrong, and L.K. Norford. 2011.  Empirical modeling of a rolling-piston compressor heat pump for predictive control in low-lift cooling.  ASHRAE Transactions 117(2).
Jiang, W., and T.A. Reddy. 2007. Combining engineering optimization of primary HVAC&R plants with decision analysis methods–Part I: Deterministic analysis. HVAC&R Research 13(1):93–117. 
Jiang, W., D. Winiarski, S. Katipamula and P.R. Armstrong. 2007. Cost-effective integration of efficient low-lift base load cooling equipment. PNNL-17157, Pacific Northwest National Laboratory, USA. 

Katipamula S., P.R. Armstrong, W. Wang, N. Fernandez, H. Cho, W. Goetzler, J. Burgos, R. Radhakrishnan, and C. Ahlfeldt. 2010. Cost-effective integration of efficient low-lift baseload cooling equipment–FY08 Final Report. PNNL-19114. Pacific Northwest National Laboratory. Richland, WA.
King, D.J. and R.A. Potter. 1988. Description of a steady-state cooling plant model developed for use in evaluating optimal control of ice thermal energy storage systems. ASHRAE Transactions 104(1):42–53.
Lau, A.S., W.A. Beckman and J.W. Mitchell. 1985. Development of computer control – routines for a large chilled water plant. ASHRAE Transactions 91(1):780–91. 

Lemmon, E.W., M.L. Huber, and M.O. McLinden. 2007. NIST Standard Reference Database 23:  Reference Fluid Thermodynamic and Transport Properties-REFPROP, Version 8.0. National Institute of Standards and Technology, Standard Reference Data Program, Gaithersburg.
Levins, W.P., C.K. Rice, and V.D. Baxter. 1997. Modeled and measured effects of compressor downsizing in an existing air conditioner/heat pump in the cooling mode. ASHRAE Transactions 192(2):22–33.
New Technology Demonstration Program (NTDP). 1994. Federal technology alert: liquid refigerant pumping. Report PNL-10232, Pacific Northwest Laboratory, Richland, WA.
Zakula, T., N.T. Gayeski, P.R. Armstrong, and L.K. Norford. 2011. Variable-speed heat pump model for a wide range of cooling conditions and loads.  HVAC&R Research 17(5):670–691.
Zakula, T. 2010. Heat Pump Simulation Model and Optimal Variable-Speed Control for a Wide Range of Cooling Conditions. Master thesis. Massachusetts Institute of Technology.

[image: image9.emf]


START 



Inputs: Q, Tz, To	
  



Create/extend 3 by 1 A-grid (ysc search)	
  



i = 1	
  



Create/extend 3 by 3 B-grid (V search)	
  



Evaluate power (E) in B-grid points for ysc=ysc{i}	
  



A{i} = B{2,2}	
  



i=i+1	
   Emin = B{2,2}?	
  



Emin = A{2}?	
  



i > 3?	
  



END 



NO 



NO 



NO 



YES 



YES 



YES 










START 

Inputs: Q, T

z

, T

o	

Create/extend 3 by 1 A-grid (y

sc

 search)	

i = 1	

Create/extend 3 by 3 B-grid (V search)	

Evaluate power (E) in B-grid points for y

sc

=y

sc

{i}	

A{i} = B{2,2}	

i=i+1	

E

min

 = B{2,2}?	

E

min

 = A{2}?	

i > 3?	

END 

NO 

NO 

NO 

YES 

YES 

YES 


Figure 1. Grid search optimization algorithm
[image: image10.emf]


To evaluate 



Known from previous step 



Minimal power 



Vo-Vo_step 



Vo+Vo_step 



Vz-Vz_step Vz+Vz_step Vz 



Vo 



Emin=B {3,2} 



STEP 1 



Vz+Vz_step Vz 



Vo 



Vo-Vo_step 



Emin=B {3,3} 



Vz+2Vz_step 



Vo+Vo_step 



STEP 2 



Vz+Vz_step 



Vo 



Emin=B {2,2} 



Vz+2Vz_step 



Vo+2Vo_step 



STEP 3 



Vz+3Vz_step 



Vo+Vo_step 










To evaluate

 

Known from previous step

 

Minimal power

 

V

o

-V

o_step 

V

o

+V

o_step 

V

z

-V

z_step 

V

z

+V

z_step 

V

z 

V

o 

E

min

=B {3,2}

 

STEP 1

 

V

z

+V

z_step 

V

z 

V

o 

V

o

-V

o_step 

E

min

=B {3,3}

 

V

z

+2V

z_step 

V

o

+V

o_step 

STEP 2

 

V

z

+V

z_step 

V

o 

E

min

=B {2,2}

 

V

z

+2V

z_step 

V

o

+2V

o_step 

STEP 3

 

V

z

+3V

z_step 

V

o

+V

o_step 


Figure 2. Search loop for the optimal air flow  (B-grid)
[image: image11.emf]


To evaluate 



Known from previous step 



Minimal power 



Vo-Vo_step 



Vo+Vo_step 



Vz-Vz_step Vz+Vz_step Vz 



Vo 



Emin=B {2,2} 



STEP 1 



Vz 



Vo 



Vo-Vo_step 



Emin=B {4,4} 



Vz+Vz_step 



Vo+Vo_step 



STEP 2 



Vz-Vz_step 










To evaluate

 

Known from previous step

 

Minimal power

 

V

o

-V

o_step 

V

o

+V

o_step 

V

z

-V

z_step 

V

z

+V

z_step 

V

z 

V

o 

E

min

=B {2,2}

 

STEP 1

 

V

z 

V

o 

V

o

-V

o_step 

E

min

=B {4,4}

 

V

z

+V

z_step 

V

o

+V

o_step 

STEP 2

 

V

z

-V

z_step 


Figure 3. Grid search step adaptation
[image: image12.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



0.5



0.6



Q/Qmax



V z (m
3 /s



)



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	












   [image: image13.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



0.5



0.6



Q/Qmax



V o (m
3 /s



)



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 4. Optimal a) evaporator and b) condenser airflow as a function of part-load ratio for To=30oC
[image: image14.emf]


0 0.2 0.4 0.6 0.8 1
0



20



40



60



80



Q/Qmax



f (
H



z)



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 5. Optimal compressor frequency as a function of part-load ratio for To=30oC
[image: image15.emf]


0 0.2 0.4 0.6 0.8 1
0



2



4



6



8



Q/Qmax



dT
sc



 (K
)



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 6. Optimal subcooling as a function of part-load ratio for To=30oC
[image: image16.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



Q/Qmax



1/
C
O
P



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 7. Specific power as a function of part-load ratio for To=30oC
[image: image17.wmf][image: image18.wmf]
Figure 8. Optimal evaporator and condenser airflow-to-compressor-frequency ratio over a wide range of conditions and loads 
[image: image19.wmf]
Figure 9. Optimal subcooling over a wide range of conditions and loads

[image: image20.emf]


Q/Qmax = 1.0	


Q/Qmax = 0.8	


Q/Qmax = 0.6	


Q/Qmax = 0.4	


Q/Qmax = 0.2	












Q/Q

max

 = 1.0	

Q/Q

max

 = 0.8	

Q/Q

max

 = 0.6	

Q/Q

max

 = 0.4	

Q/Q

max

 = 0.2	


Figure 10. Specific power over a wide range of conditions and loads
[image: image21.wmf]   [image: image22.wmf]
Figure 11. COP relative difference for a) optimal versus zero subcooling case and b) optimal versus fixed air flow and zero subcooling case, all for Tz=22oC

[image: image23.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



Q/Qmax



1/
C
O
P



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 12. Specific power as a function of part-load ratio for single-compressor machine (solid line) and two-compressor machine with each compressor sized for half Qmax (dashed line), all for To=30oC. Specific power is the same for both machines above ~50% part-load.

[image: image24.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



Q/Qmax



1/
C
O
P



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	












   [image: image25.emf]


0 0.2 0.4 0.6 0.8 1
0



0.1



0.2



0.3



0.4



Q/Qmax



1/
C
O
P



Tz  = 30oC	


Tz = 26oC	


Tz = 22oC	


Tz = 18oC	













Figure 13. Economizer mode (dashed line) and compressor mode (solid line) for a) To=15oC and b) To=20oC 
[image: image26.emf]


0
0.5



1 −10 0 10 20 30 40



0



50



100



150



200



250



300



T
o
 (oC)Q/Q



max



C
O



P











Figure 14. Combined COP (compressor and economizer mode) for Tz=22oC
[image: image27.wmf]   [image: image28.wmf]
Figure 15. COP relative difference for a) ammonia versus R410A case and b) propane versus R410A case, all for Tz=22o
[image: image29.wmf]  [image: image30.wmf]
Figure 16. Cooling load distributions: A-without, B-with thermal energy storage

[image: image31.wmf]
Figure 17. Heat pump optimal sizing for FLEOH distribution A with variable-speed heat pump (blue), FLEOH distribution A with two-speed heat pump (green) and FLEOH distribution B with variable-speed heat pump (red) 

1
PAGE  
2

_1263657221.unknown

_1265008262.unknown

_1265008263.unknown

_1265098557.unknown

_1265008260.unknown

_1263657132.unknown

_1263657174.unknown

_1263565761.unknown

